## Filter_master
Filter_type | Test_dust | Experiment_N | Filter_ID | Date | Start_time | Loading_area_type | Loading_area_loc | M_filter_blank | Petridish_w_dust_m | Petridish_wo_dust_m | Pre_hepa_sampler_m | Post_hepa_sampler_m | M_filter_pre | Dust_sprinkled_m | Filter_m_change | Flow_dust_m | Lost_dust_m | Mass_closure | Loading_eff | Hepa_eff | td_sample_old | gf_sample_old | ex_sample_old | si_sample_old | Test_purpose | td_sample | gf_sample | ex_sample | si_sample
14e | ash2 | 019 | test_012 | 180405 | 14:10 | half | 1 | 391.029 | 5.3724 | 3.3637 | 18.2504 | 18.2523 | 393.017 | 2.0087 | 1.988 | 0.00196 | 0.01874 | 99.0671 | 98.9695 | 9.4686 | Replicate#3:ASHRAE#2STD |  | 019_ext_180405_am | 019_sie_180405_am |  | RN31Replicat_ | #N/A | RN1_019_ext__ | RN6_019_sie__
11e | ash2 | 001 | Test_001 | 171128 |  | Full | 1 | 260.225 | 37.9966 | 22.8697 |  |  | 275.054 | 15.1269 | 14.829 |  | 0.29791 | 98.0306 | 98.0306 | 0 | Replicate#3:ASHRAE#2STD |  | HVAC_Filter_Dust_Loading_ASHRAE#2_Sieved1m |  | Initial test: to see how much we can extract, 15 gr tested equivalent to site 6 reported in ASHRAE paper | RN31Replicat_ | #N/A | RN11HVAC_Fil_ | #N/A
11e | iso2 | 010 | Test_005 | 180326 | 13:24 | Full | 1 | 280.852 | 18.0466 | 3.3619 | 72.8399 | 73.0777 | 294.459 | 14.6847 | 13.607 | 0.2378 | 0.83995 | 94.2801 | 92.6608 | 22.0646 | A2_STD_180326_am | tnn_bk1_180326_am | tnn_ext_180326_am_1 |  |  | RN21A2_STD_1_ | RN1tnn_bk1__1 | RN6tnn_ext__1 | #N/A
11e | iso2 | 014 | Test_008 | 180403 | 13:11 | Full | 1 | 276.908 | 8.3575 | 3.2904 | 21.499 | 21.8783 | 280.349 | 5.0671 | 3.441 | 0.37926 | 1.2468 | 75.3936 | 67.9088 | 23.3234 | A2_STD_180326_am | 014_bk1_180403_am | 014_ext_180403_am |  | Base-case with new protocol launched - rep 3 | RN21A2_STD_1_ | RN12_014_bk1_ | RN11_014_ext_ | #N/A
11e | ash2 | 004 | Test_002 | 180221 |  | Quarter | 4 | 262.978 | 12.6236 | 8.4917 | 14.939 | 15.0015 | 266.567 | 4.1319 | 3.589 | 0.06256 | 0.48031 | 88.3755 | 86.8614 | 11.5239 | Replicate#3:ASHRAE#2STD | M2_ASHRAE#2 | Sock_ASHRAE#2 | Sieve_ASHRAE#2 | Test to see how eq 16 g per filter works | RN31Replicat_ | RN1M2_ASHRA_1 | RN6Sock_ASH_1 | RN11Sieve_AS_
11e | ash2 | 002 | Test_002 | 180216 |  | Quarter | 1 | 286.73 | 27.0324 | 22.8946 |  |  | 290.288 | 4.1378 | 3.558 |  | 0.57977 | 85.9883 | 85.9883 | 0 | Replicate#3:ASHRAE#2STD | ASHRAE#2_MPD2 | Extract_below1m_ASHRAE#2_MERV11E | Extract_ASHRAE#2_MERV11_Above1mm | Test to see how eq 16 g per filter works | RN31Replicat_ | RN6ASHRAE_2_1 | RN11Extract__ | RN21Extract__
11e | ash2 | 005 | Test_002 | 180226 |  | Quarter | 3 | 264.435 | 7.5861 | 3.3647 | 14.9089 | 15.0515 | 268.008 | 4.2215 | 3.573 | 0.14265 | 0.50581 | 88.0181 | 84.639 | 21.9983 | Replicate#3:ASHRAE#2STD | M2_ASHRAE#2_180226 | ASHRAE#2_<1mm_CouplerTap |  | Test to see how eq 16 g per filter works | RN31Replicat_ | RN1M2_ASHRA_1 | RN11ASHRAE_2_ | #N/A
11e | iso2 | 003 | Test_003 | 180216 |  | Quarter | 1 | 284.407 | 7.3484 | 3.3591 | 14.9117 | 15.0397 | 287.676 | 3.9893 | 3.269 | 0.128 | 0.59231 | 85.1526 | 81.944 | 17.7701 | A2_STD_180326_am | ISOA2_PD2Mass | ISO_A1_Extract_Below1m |  | Test to see how eq 16 g per filter works | RN21A2_STD_1_ | RN31ISOA2_PD_ | RN36ISO_A1_E_ | #N/A
11e | ash2 | 015 | Test_009 | 180403 | 14:45 | Half | 2 | 284.863 | 5.8073 | 3.2924 | 18.0471 | 18.1838 | 286.85 | 2.5148 | 1.987 | 0.13671 | 0.39111 | 84.4478 | 79.0116 | 25.9009 | Replicate#3:ASHRAE#2STD | 015_bk1_180403_am | 015_ext_180403_am |  |  | RN31Replicat_ | RN16_015_bk1_ | RN21_015_ext_ | #N/A
11e | iso2 | 013 | Test_007 | 180403 | 10:38 | Half | 2 | 285.721 | 6.292 | 3.2914 | 18.2341 | 18.4017 | 287.926 | 3.0006 | 2.205 | 0.16756 | 0.62804 | 79.0695 | 73.4853 | 21.0608 | A2_STD_180326_am | 013_bk1_180403_am | 013_ext_180403_am |  | Base-case with new protocol launched - rep 2 | RN21A2_STD_1_ | RN11_013_bk1_ | RN16_013_ext_ | #N/A
11e | ash2 | 009 | Test_002 | 180312 |  | Quarter | 2 | 290.872 | 4.4678 | 3.3601 | 18.6332 |  | 291.664 | 1.1077 | 0.792 |  | 0.31571 | 71.4989 | 71.4989 | 0 | Replicate#3:ASHRAE#2STD | Flow_dust_ASHRAE#2_1gr | Extract_ASHRAE#2_MERV11E |  |  | RN31Replicat_ | RN11Flow_dus_ | RN16Extract__ | #N/A
08m | ash2 | 021 | test_014 | 180406 | 14:45 | half | 1 | 255.647 | 5.8205 | 3.2963 | 19.6218 | 19.7687 | 257.433 | 2.5242 | 1.786 | 0.14687 | 0.59134 | 76.5733 | 70.7548 | 19.8954 | Replicate#3:ASHRAE#2STD | 021_bk1_180406_am | 021_ext_180406_am | 021_sie_180406_am |  | RN31Replicat_ | RN1_021_bk1__ | RN6_021_ext__ | RN11_021_sie_
14e | iso2 | 018 | Test_011 | 180405 | 13:04 | Half | 1 | 391.395 | 5.3542 | 3.3569 | 18.2504 | 18.2385 | 393.342 | 1.9973 | 1.947 | -0.01182 | 0.06215 | 96.8883 | 97.4801 | -23.485 | A2_STD_180326_am |  | 018_ext_180405_am_r2 |  |  | RN21A2_STD_1_ | #N/A | RN6_018_ext__ | #N/A
11e | iso2 | 012 | Test_007 | 180403 | 9:30 | Half | 1 | 285.167 | 5.2878 | 3.291 | 14.9711 | 15.1507 | 286.424 | 1.9967 | 1.257 | 0.17958 | 0.56016 | 71.9463 | 62.9526 | 24.2761 | A2_STD_180326_am | 012_bk1_180403_am | 012_ext_180403_am |  | Base-case with new protocol launched | RN21A2_STD_1_ | RN17_012_bk1_ | RN16_012_ext_ | #N/A
08e | iso2 | 016 | Test_006 | 180405 | 9:30 | Half | 2 | 257.932 | 5.8484 | 3.2906 | 19.9691 | 20.4876 | 259.109 | 2.5578 | 1.177 | 0.51855 | 0.8622 | 66.2907 | 46.017 | 37.5557 | A2_STD_180326_am | 016_bk1_180405_am | 016_ext_180405_am |  |  | RN21A2_STD_1_ | RN1_016_bk1__ | RN11_016_ext_ | #N/A
08e | ash2 | 017 | Test_010 | 180405 | 10:28 | Half | 1 | 256.74 | 5.86 | 3.2916 | 19.8861 | 20.1769 | 258.178 | 2.5684 | 1.438 | 0.29076 | 0.8396 | 67.3099 | 55.989 | 25.7228 | Replicate#3:ASHRAE#2STD | 017_bk1_180405_am | 017_ext_180405_am | 017_sie_180405_am |  | RN31Replicat_ | RN1_017_bk1__ | RN6_017_ext__ | RN11_017_sie_
08m | iso2 | 020 | test_013 | 180406 | 13:45 | half | 1 | 271.541 | 5.9048 | 3.3634 | 19.6069 | 19.9854 | 272.701 | 2.5415 | 1.16 | 0.37853 | 1.0029 | 60.5375 | 45.6432 | 27.4009 | A2_STD_180326_am | 020_bk2_180406_am | 020_ext_180406_am |  |  | RN21A2_STD_1_ | RN1_020_bk2__ | RN6_020_ext__ | #N/A
11e | iso2 | 007 | Test_003 | 180312 |  | Quarter | 3 | 285.06 | 4.4964 | 3.0685 | 18.2165 | 18.2999 | 286.05 | 1.4279 | 0.99 | 0.08346 | 0.35445 | 75.177 | 69.3321 | 19.0587 | A2_STD_180326_am |  |  |  |  | RN21A2_STD_1_ | #N/A | #N/A | #N/A
11e | iso1 | 008 | Test_004 | 180312 |  | Quarter | 1 | 285.754 | 4.2847 | 3.2957 | 18.4195 | 18.4472 | 286.206 | 0.98901 | 0.452 | 0.02773 | 0.50928 | 48.5061 | 45.7023 | 5.1638 |  | Flow_dust_A1 | Extract_dust_A1 |  |  | #N/A | RN1Flow_dus_1 | RN6Extract__1 | #N/A
08e | iso2 | 011 | Test_006 | 180328 | 9:30 | Half | 1 | 260.785 | 5.3472 | 3.3608 | 36.7998 | 37.0201 | 261.591 | 1.9864 | 0.806 | 0.22036 | 0.96004 | 51.6694 | 40.5759 | 18.6682 | A2_STD_180326_am | Dust_Flow/grav_011 | Extract_011 |  | To measure the initial test with new version of protocol | RN21A2_STD_1_ | RN36Dust_Flo_ | RN41Extract__ | #N/A
11e | iso2 | 006 | Test_003 | 180307 |  | Quarter | 2 | 288.191 | 4.4159 | 3.2915 | 28.147 | 28.2598 | 288.808 | 1.1244 | 0.617 | 0.11282 | 0.39462 | 64.9052 | 54.8718 | 22.2332 | A2_STD_180326_am | A2_M2_180307_am | A2_extract_180307_am |  |  | RN21A2_STD_1_ | RN6A2_M2_18_1 | RN1A2_extra_1 | #N/A

## Loading_variable_description
Variable | Description | Type | Called in Steps | Comment
Filter_type | Identified by efficiency (e.g., MERV8m, MERV8e, MERV11e, and MERV14e) | Known | 1
Test_dust | Type of the standard test dust (STD) with which filter is loaded | Known | 1
Test_# | A number given to each test to distinguish it from the other tests | Input | 1
Filter_ID | A three digit number given to distinguish filters (e.g., 001, 002, etc.) | Input | 1
Date | Date you do loading test | Input | 1
Start_time | Time (hh:mm) you start loading the filter | Input | 1
Loading_area_type | Fraction of the filter you want to load with dust (e.g., quarter, half, whole) | Input | 2
Loading_area_loc | Location of the filter area fraction you want to load the filter with * | Input | 2
Test_purpose | A clear reason illuminating why test is taken, preferabbly stated in a short sentence | Input | 2
M_filter_blank | Mass of a preload filter (not loaded yet) + the mass of the antistatic bag + mass of hook | Measured | 4
Petridish_w_dust_m | Mass of petridish#1 + total dust to be loaded on the filter | Measured | 8
Petridish_w/o_dust_m | Mass of petridish#1 after the total dust to be loaded on the filter is sprinkled over the filter | Measured | 10
Pre_hepa_sampler_m | Mass of petridish#3 plus commercial sampler (full assembley) before artificial final loading stage | Measured | 19
Post_hepa_sampler_m | Mass of petridish#3 plus commercial sampler (full assembley) after artificial final loading stage | Measured | 23
M_filter_pre | Mass of a postload filter (initially and finally loaded) + the mass of the antistatic bag + mass of hook | Measured | 24
Pre_gravimetric_m | Mass of petridish#2 | Measured | 12 | Typically, no gravity dust is evident for MERV filters
Post_gravimetric_m | Mass of petridish#2 + plus the dust passing through by gravity | Measured | 14 | Typically, no gravity dust is evident for MERV filters
Dust_sprinkled_m | Total mass of the dust sprinkled over the filter | Calculated | 7
Filter_m_change | Mass of dust loaded in the filter | Calculated | 24
Flow_dust_m | Mass of dust passing through during the final loading stage (by aritificial flow) | Calculated | 23
Gravity_dust_m | Mass of dust passing through the filter during the initial loading stage (by gravity) | Calculated | 14
Bag_left_dust_m | Mass of dust left in the bag not appropriately loaded on the filter | Calculated | 25
Lost_dust_m | Mass of the dust disappeared during the whole procedure | Calculated | n.a
Mass_closure | Ratio of sum of observations 20-23 to observation 19 in percentages | Evaluated | 32
Loading_eff | Ratio of the dust loaded in the filter to the total dust mass sprinkled over the filter in percentages | Evaluated | 32
*
1, 2, 3, and 4 if you go quarter by quarter (location defiened based on trigonometriy circle quarters);
1, 2, and 3 if you want to go two quarters first, and one half last;
1,3, and 4 if you want to go one half first amd two quarters last;
1, and 3 if you want to do two quarters
1 if you want to do whole

## Notes
Comment # | Comment Description | Subcomment description
1 | In the first observation (test # 001) I swat negligible mass for both flow_ and gravimetric_dust; I didn't bother measureing them
1.1 |  | The final loadig stage in this observation was based on not touching the commercial sampler to the filter downstream but keeping it colse enough
2 | test#14: some dust dumped from commercial sampler during th handling
3 | All the tests prior to #9 could have cross-contamination. This might not be an issue with larger masses (equal 16 g per filter)
3.1 |  | Observations #6-9 could be the most vulnerable data
4 | Experiment #09 corrupted, one data piece not recorded
5 | Experiment #11: I susect the mass you collected in the bag (dust left) is from previous experiments. This is because we never had this situation taking place again (i.e., enough mass left inside a bag such that you can reverse the bag and shake it to get the dust)
6 | Experiment#2 has pre_hepa_sampler_m as 36.3522 + REF!, it is not clear what REF! has been, so I simply delete this cell and its adjacent cell Post_hepa_sampler_m which has a value of 38.04376
7 | The iso a2 TD sample argument has a typo in its name, it is in fact A2 not A1
8 | HVAC_Filter_Dust_Loading_ASHRAE#2_Sieved1m | has another same name w density of 2 (should be removed from the list)
9 | test 005 has two extracts, one w coupler tap and one w/o coupler tap; before 005 every thing might have been w/o tap
10 | 008 csv was named after 007, get 007 from MS again
11 | 010 has multiple sample names: ext has two replicates _1 and _2 (the second one has bk1 but it is actually ext); one rep before A2_STD is the dust in bag; however we do not consider it
12 | 012 had some bad data that I manually got rid off
13 | 015 two reps with very similar PSD for ext. I got the first. In these casese refer to 1 becz 2 is only a conf for device accuracy
14 | For 018 we do not have gf sample

## names
samplename | recordnumber | varinfo
012_bk1_180403_am | 17 | RN17_012_bk1_
012_ext_180403_am | 16 | RN16_012_ext_
013_bk1_180403_am | 11 | RN11_013_bk1_
013_ext_180403_am | 16 | RN16_013_ext_
014_bk1_180403_am | 12 | RN12_014_bk1_
014_ext_180403_am | 11 | RN11_014_ext_
015_bk1_180403_am | 16 | RN16_015_bk1_
015_ext_180403_am | 21 | RN21_015_ext_
015_ext_1880403_am_r2 | 26 | RN26_015_ext_
016_bk1_180405_am | 1 | RN1_016_bk1__
016_bk1_180405_am_r2 | 6 | RN6_016_bk1__
016_ext_180405_am | 11 | RN11_016_ext_
017_bk1_180405_am | 1 | RN1_017_bk1__
017_ext_180405_am | 6 | RN6_017_ext__
017_sie_180405_am | 11 | RN11_017_sie_
018_ext_180405_am | 1 | RN1_018_ext__
018_ext_180405_am_r2 | 6 | RN6_018_ext__
019_ext_180405_am | 1 | RN1_019_ext__
019_sie_180405_am | 6 | RN6_019_sie__
020_bk2_180406_am | 1 | RN1_020_bk2__
020_ext_180406_am | 6 | RN6_020_ext__
021_bk1_180406_am | 1 | RN1_021_bk1__
021_com_180406_am | 16 | RN16_021_com_
021_ext_180406_am | 6 | RN6_021_ext__
021_sie_180406_am | 11 | RN11_021_sie_
A2_M2_180307_am | 6 | RN6A2_M2_18_1
A2_STD_180326_am | 21 | RN21A2_STD_1_
A2_extract_180307_am | 1 | RN1A2_extra_1
ASHRAE#2STD | 1 | RN1ASHRAE_2_1
ASHRAE#2_<1mm_CouplerTap | 11 | RN11ASHRAE_2_
ASHRAE#2_<1mm_Coupler_Tap | 6 | RN6ASHRAE_2_1
ASHRAE#2_MPD2 | 6 | RN6ASHRAE_2_1
ASHRAE#2_STD | 1 | RN1ASHRAE_2_1
Dust_Flow/grav_011 | 36 | RN36Dust_Flo_
Dust_Left_001 | 31 | RN31Dust_Lef_
Extract_011 | 41 | RN41Extract__
Extract_ASHRAE#2_MERV11E | 16 | RN16Extract__
Extract_ASHRAE#2_MERV11_Above1mm | 21 | RN21Extract__
Extract_below1m_ASHRAE#2_MERV11E | 11 | RN11Extract__
Extract_dust_A1 | 6 | RN6Extract__1
Flow_dust_A1 | 1 | RN1Flow_dus_1
Flow_dust_ASHRAE#2_1gr | 11 | RN11Flow_dus_
HVAC_Filter_Dust_Loading_ASHRAE#2_Sieved1m | 11 | RN11HVAC_Fil_
ISOA1_STD | 26 | RN26ISOA1_ST_
ISOA2_PD2Mass | 31 | RN31ISOA2_PD_
ISO_A1_Extract_Below1m | 36 | RN36ISO_A1_E_
M2_ASHRAE#2 | 1 | RN1M2_ASHRA_1
M2_ASHRAE#2_180226 | 1 | RN1M2_ASHRA_1
Previous_Run2 | 16 | RN16Previous_
Replicate#3:ASHRAE#2STD | 31 | RN31Replicat_
Rerplicate2:ASHRAE#2STD | 21 | RN21Rerplica_
Sieve_ASHRAE#2 | 11 | RN11Sieve_AS_
Sock_ASHRAE#2 | 6 | RN6Sock_ASH_1
tnn_bk1_180326_am | 1 | RN1tnn_bk1__1
tnn_bk1_180326_am_2 | 11 | RN11tnn_bk1__
tnn_ext_180326_am_1 | 6 | RN6tnn_ext__1